UNINTRUPTABLE POWER SUPPLY (U.P.S)

TABLE OF CONTENT

- Common power problems

- Technologies

  - Offline / standby

  - Line-interactive

  - Double-conversion / online

  - Hybrid topology / Double conversion on demand

  - Ferro-resonant

  - DC power

  - Rotary

- Applications

  - N+1

  - Multiple redundancy

  - Outdoor use

  - Internal systems

- Machine standards

  - Measuring efficiency

  - Warranty

- Difficulties faced with generator use

  - Frequency variations

  - Power factor

- Communication

- Calculating on-battery runtime[6]

- See also

- Notes

- References

- External links

## INTRODUCTION:

An uninterruptible power supply, also uninterruptible power source, UPS or battery/flywheel backup, is an electrical apparatus that provides emergency power to a load when the input power source, typically the utility mains, fails. A UPS differs from an auxiliary or emergency power system orstandby generator in that it will provide instantaneous or near-instantaneous protection from input power interruptions by means of one or more attachedbatteries and associated electronic circuitry for low power users, and or by means of diesel generators and flywheels for high power users. The on-battery runtime of most uninterruptible power sources is relatively short—5–15 minutes being typical for smaller units—but sufficient to allow time to bring an auxiliary power source on line, or to properly shut down the protected equipment.

While not limited to protecting any particular type of equipment, a UPS is typically used to protect computers, data centers, telecommunicationequipment or other electrical equipment where an unexpected power disruption could cause injuries, fatalities, serious business disruption and/or data loss. UPS units range in size from units designed to protect a single computer without a video monitor (around 200 VA rating) to large units powering entire data centers, buildings, or even cities.[1]

## Common power problems

The primary role of any UPS is to provide short-term power when the input power source fails. However, most UPS units are also capable in varying degrees of correcting common utility power problems:

- Power failure: defined as a total loss of input voltage.

- Surge: defined as a momentary or sustained increase in the mains voltage.

- Sag: defined as a momentary or sustained reduction in input voltage.

- Spikes, defined as a brief high voltage excursion.

- Noise, defined as a high frequency transient or oscillation, usually injected into the line by nearby equipment.

- Frequency instability: defined as temporary changes in the mains frequency.

- Harmonic distortion: defined as a departure from the ideal sinusoidal waveform expected on the line.

UPS units are divided into categories based on which of the above problems they address[dubious – discuss], and some manufacturers categorize their products in accordance with the number of power related problems they address.

## Technologies

The general categories of modern UPS systems are on-line, line-interactive or standby. An on-line UPS uses a "double conversion" method of accepting AC input, rectifying to DC for passing through therechargeable battery (or battery strings), then inverting back to 120V/240V AC for powering the protected equipment. A line-interactive UPS maintains the inverter in line and redirects the battery's DC current path from the normal charging mode to supplying current when power is lost. In a standby ("off-line") system the load is powered directly by the input power and the backup power circuitry is only invoked when the utility power fails. Most UPS below 1 kVA are of the line-interactive or standby variety which are usually less expensive.

For large power units, dynamic uninterruptible power supplies are sometimes used. A synchronous motor/alternator is connected on the mains via a choke. Energy is stored in a flywheel. When the mains power fails, an Eddy-current regulation maintains the power on the load. DUPS are sometimes combined or integrated with a diesel-generator[clarification needed], forming a diesel rotary uninterruptible power supply, orDRUPS.

A fuel cell UPS has been developed in recent years using hydrogen and a fuel cell as a power source, potentially providing long run times in a small space.

## Offline / standby

Offline / standby UPS. Typical protection time: 0–20 minutes. Capacity expansion: Usually not available

The Offline / Standby UPS (SPS) offers only the most basic features, providing surge protection and battery backup. With this type of UPS, a user's equipment is normally connected directly to incoming utility power with the same voltage transient clamping devices used in a common surge protected plug strip connected across the power line. When the incoming utility voltage falls below a predetermined level the SPS turns on its internal DC-AC inverter circuitry, which is powered from an internal storage battery. The SPS then mechanically switches the connected equipment on to its DC-AC inverter output. The switchover time can be as long as 25 milliseconds depending on the amount of time it takes the Standby UPS to detect the lost utility voltage. Generally speaking, dependent on the size of UPS connected load and the sensitivity of the connected equipment to voltage variation, the UPS will be designed and/or offered (specification wise) to cover certain ranges of equipment, i.e. Personal Computer, without any obvious dip or brownout to that device.

## Line-interactive

Line-Interactive UPS. This illustration shows an isolated transformer, not an autotransformer, and does not show the way that the charger and inverter are connected to the secondary side of the same transformer. Typical protection time: 5–30 minutes. Capacity expansion: Several hours

The Line-Interactive UPS is similar in operation to a Standby UPS, but with the addition of a multi-tap variable-voltage autotransformer. This is a special type of electrical transformer that can add or subtract powered coils of wire, thereby increasing or decreasing the magnetic field and the output voltage of the transformer.

This type of UPS is able to tolerate continuous undervoltage brownouts and overvoltage surges without consuming the limited reserve battery power. It instead compensates by automatically selecting different power taps on the autotransformer. Depending on the design, changing the autotransformer tap can cause a very brief output power disruption,[citation needed] which may cause UPSs equipped with a power-loss alarm to "chirp" for a moment.

This has become popular even in the cheapest UPSs because it takes advantage of components already included. The main 50/60 Hz transformer used to convert between line voltage and battery voltage needs to provide two slightly different turns ratios: one to convert the battery output voltage (typically a multiple of 12 V) to line voltage, and a second one to convert the line voltage to a slightly higher battery charging voltage (such as a multiple of 14 V). Further, it is easier to do the switching on the line-voltage side of the transformer because of the lower currents on that side.

To gain the buck/boost feature, all that is required is two separate switches so that the AC input can be connected to one of the two primary taps, while the load is connected to the other, thus using the main transformer's primary windings as an autotransformer. Note that the battery can still be charged while "bucking" an overvoltage, but while "boosting" an undervoltage, the transformer output is too low to charge the batteries.

Autotransformers can be engineered to cover a wide range of varying input voltages, but this requires more taps and increases complexity, and expense of the UPS. It is common for the autotransformer to only cover a range from about 90 V to 140 V for 120 V power, and then switch to battery if the voltage goes much higher or lower than that range.

In low-voltage conditions the UPS will use more current than normal so it may need a higher current circuit than a normal device. For example to power a 1000 watt device at 120 volts, the UPS will draw 8.32 amps. If a brownout occurs and the voltage drops to 100 volts, the UPS will draw 10 amps to compensate. This also works in reverse, so that in an overvoltage condition, the UPS will need fewer amps of current.

## Double-conversion / online

Typical protection time:

5 – 30 minutes

Capacity expansion:

Several hours

The online UPS is ideal for environments where electrical isolation is necessary or for equipment that is very sensitive to power fluctuations. Although once previously reserved for very large installations of 10 kW or more, advances in technology have permitted it to now be available as a common consumer device, supplying 500 watts or less. The online UPS is generally more expensive but may be necessary when the power environment is "noisy" such as in industrial settings, for larger equipment loads like data centers, or when operation from an extended-run backup generator is necessary.

The basic technology of the online UPS is the same as in a standby or Line-Interactive UPS. However it typically costs much more, due to it having a much greater current AC-to-DC battery-charger/rectifier, and with the rectifier and inverter designed to run continuously with improved cooling systems. It is called a Double-Conversion UPS due to the rectifier directly driving the inverter, even when powered from normal AC current.

In an online UPS, the batteries are always connected to the inverter, so that no power transfer switches are necessary. When power loss occurs, the rectifier simply drops out of the circuit and the batteries keep the power steady and unchanged. When power is restored, the rectifier resumes carrying most of the load and begins charging the batteries, though the charging current may be limited to prevent the high-power rectifier from overheating the batteries and boiling off the electrolyte.

The main advantage to the on-line UPS is its ability to provide an electrical firewall between the incoming utility power and sensitive electronic equipment. While the standby and Line-Interactive UPS merely filter the input utility power, the Double-Conversion UPS provides a layer of insulation from power quality problems. It allows control of output voltage and frequency regardless of input voltage and frequency.

### Hybrid topology / Double conversion on demand

Recently there have been hybrid topology UPSs hitting the marketplace. These hybrid designs do not have an official designation, although one name used by HP and Eaton is Double Conversion on Demand.[2]This style of UPS is targeted towards high efficiency applications while still maintaining the features and protection level offered by double conversion.

A hybrid (double conversion on demand) UPS operates as an off-line/standby UPS when power conditions are within a certain preset window. This allows the UPS to achieve very high efficiency ratings. When the power conditions fluctuate outside of the predefined windows, the UPS switches to online/double conversion operation.[2] In double conversion mode the UPS can adjust for voltage variations without having to use battery power, can filter out line noise and control frequency. Examples of this hybrid/double conversion on demand UPS design are the HP R8000, HP R12000, HP RP12000/3 and the Eaton BladeUPS.

### Ferro-resonant

Typical protection time:

5 - 15 Minutes

Capacity expansion:

Several Hours

Ferro-resonant units operate in the same way as a standby UPS unit however they are online with the exception that a ferro-resonant transformer is used to filter the output. This transformer is designed to hold energy long enough to cover the time between switching from line power to battery power and effectively eliminates the transfer time. Many ferro-resonant UPSs are 82–88% efficient (AC-DC-AC) and offer excellent isolation.

The transformer has three windings, one for ordinary mains power, the second for rectified battery power, and the third for output AC power to the load.

This used to be the dominant type of UPS and is limited to around the 150 kVA range. These units are still mainly used in some industrial settings (Oil and Gas, Petrochemical, Chemical, Utility, and Heavy Industry markets) due to the robust nature of the UPS. Many ferro-resonant UPSs utilizing controlled ferro technology may not interact with power-factor-correcting equipment.

### DC power

Typical protection time:

Several hours

Capacity expansion:

Yes

A UPS designed for powering DC equipment is very similar to an online UPS, except that it does not need an output inverter, and often the powered device does not need a power supply. Rather than converting AC to DC to charge batteries, then DC to AC to power the external device, and then back to DC inside the powered device, some equipment accepts DC power directly and allows one or more conversion steps to be eliminated. This equipment is more commonly known as a rectifier.

Many systems used in telecommunications use 48 V DC power, because it is not considered a high-voltage by most electrical codes and is exempt from many safety regulations, such as being installed in conduit and junction boxes. DC has typically been the dominant power source for telecommunications, and AC has typically been the dominant source for computers and servers.

There has been much experimentation with 48 V DC power for computer servers, in the hope of reducing the likelihood of failure and the cost of equipment. However, to supply the same amount of power, the current must be greater than an equivalent 120 V or 240 V circuit, and greater current requires larger conductors and/or more energy to be lost as heat.

High voltage DC (380 V) is finding use in some data center applications, and allows for small power conductors, but is subject to the more complex electrical code rules for safe containment of high voltages.

Most switched-mode power supply (SMPS) power supplies for PCs can handle 325 V DC (230 V mains voltage × √2) directly, because the first thing they do to the AC input is rectify it. This does cause unbalanced heating in the input rectifier stage as the full load passes through only half of it, but that is not generally a significant problem. (Power supplies with a 115/230 V switch operate as a voltage doubler when in the 115 V position, which does require AC power, but the voltage doubler configuration also uses only half the rectifier, so it is certain to be able to handle the unbalance when operated from DC in the 230 V position.)

### Rotary

Typical protection time:

20 – 60 seconds

Capacity expansion:

Several seconds

A Rotary UPS uses the inertia of a high-mass spinning flywheel (Flywheel energy storage) to provide short-term ride-through in the event of power loss. The flywheel also acts as a buffer against power spikes and sags, since such short-term power events are not able to appreciably affect the rotational speed of the high-mass flywheel. It is also one of the oldest designs, predating vacuum tubes and integrated circuits.

It can be considered to be on line since it spins continuously under normal conditions. However, unlike a battery-based UPS, flywheel based UPS systems typically provide 10 to 20 seconds of protection before the flywheel has slowed and power output stops. It is traditionally used in conjunction with standby diesel generators, providing backup power only for the brief period of time the engine needs to start running and stabilize its output.

The Rotary UPS is generally reserved for applications needing more than 10,000 watts of protection, to justify the expense and benefit from the advantages rotary UPS systems bring. A larger flywheel or multiple flywheels operating in parallel will increase the reserve running time or capacity.

Because the flywheels are a mechanical power source, it is not necessary to use an electric motor or generator as an intermediary between it and a diesel engine designed to provide emergency power. By using a transmission gearbox,

the rotational inertia of the flywheel can be used to directly start up a diesel engine, and once running, the diesel engine can be used to directly spin the flywheel. Multiple flywheels can likewise be connected in parallel through mechanical countershafts, without the need for separate motors and generators for each flywheel.

They are normally designed to provide very high current output compared to a purely electronic UPS, and are better able to provide inrush current for inductive loads such as motor startup or compressor loads, as well as medical MRI and cath lab equipment. It is also able to tolerate short-circuit conditions up to 17 times larger than an electronic UPS, permitting one device to blow a fuse and fail while other devices still continue to be powered from the Rotary UPS.

Its life cycle is usually far greater than a purely electronic UPS, up to 30 years or more. But they do require periodic downtime for mechanical maintenance, such as ball bearing replacement. In larger systems redundancy of the system ensures the availability of processes during this maintenance. Battery-based designs do not require downtime if the batteries can be hot-swapped, which is usually the case for larger units. Newer Rotary units use technologies such as Magnetic bearings and air-evacuated enclosures to increase standby efficiency and reduce maintenance to very low levels.

Typically, the high-mass flywheel is used in conjunction with a motor-generator system. These units can be configured as:[4]

- A motor driving a mechanically connected generator,

- A combined synchronous motor and generator wound in alternating slots of a single rotor and stator,

- A hybrid rotary UPS, designed similar to an online UPS, except that it uses the flywheel in place of batteries. The rectifier drives a motor to spin the flywheel, while a generator uses the flywheel to power the inverter.

In case #3 the motor generator can be synchronous/synchronous or induction/synchronous. The motor side of the unit in case #2 and #3 can be driven directly by an AC power source (typically when in inverter bypass), a 6-step double-conversion motor drive, or a 6 pulse inverter. Case #1 uses an integrated flywheel as a short-term energy source instead of batteries to allow time for external, electrically coupled gensets to start and be brought online. Case #2 and #3 can use batteries or a free-standing electrically coupled flywheel as the short-term energy source.

### Applications

### N+1

In large business environments where reliability is of great importance, a single huge UPS can also be a single point of failure that can disrupt many other systems. To provide greater reliability, multiple smaller UPS modules and batteries can be integrated together to provide redundant power protection equivalent to one very large UPS. "N+1" means that if the load can be supplied by N modules, the installation will contain N+1 modules. In this way, failure of one module will not impact system operation.

### Multiple redundancy

Many computer servers offer the option of redundant power supplies, so that in the event of one power supply failing, one or more other power supplies are able to power the load. This is a critical point - each power supply must be able to power the entire server by itself.

Redundancy is further enhanced by plugging each power supply into a different circuit (i.e. to a different circuit breaker).

Redundant protection can be extended further yet by connecting each power supply to its own UPS. This provides double protection from both a power supply failure and a UPS failure, so that continued operation is assured. This configuration is also referred to as 2N redundancy. If the budget does not allow for two identical UPS units then it is common practice to plug one power supply into mains power and the other into the UPS.

### Outdoor use

When a UPS system is placed outdoors, it should have some specific features that guarantee that it can tolerate weather with a 'minimal to none' effect on performance. Factors such as temperature, humidity, rain, and snow among others should be considered by the manufacturer when designing an outdoor UPS system. Operating temperature ranges for outdoor UPS systems could be around −40 °C to +55 °C.

Outdoor UPS systems can be pole, ground (pedestal), or host mounted. Outdoor environment could mean extreme cold, in which case the outdoor UPS system should include a battery heater mat, or extreme heat, in which case the outdoor UPS system should include a fan system or an air conditioning system.

### Internal systems

UPS systems can be designed to be placed inside a computer chassis. There are two types of internal UPS. The first type is a miniaturized regular UPS that is made small enough to fit into a 5.25-inch CD-ROM slot bay of a regular computer chassis. The other type are re-engineered switching power supplies that utilize dual power sources of AC and/or DC as power inputs and have an AC/DC built-in switching management control units.

### Machine standards

The way efficiency is measured varies massively in the UPS market, and there are a number of reasons for this. Many UPS manufacturers claim to have the highest level of efficiency, often using different sets of criteria in order to reach these figures. The industry norm can be argued to be anything between 93%-96% when a UPS is in full operational mode, and to reach these figures companies often put their UPS in an ideal scenario. Efficiency figures on site are often much closer to the 90% mark, due to varying power conditions. The perfect scenario will never happen in reality, due to ongoing voltage sags from the mains and the declining efficiency of UPS batteries.

### Warranty

Warranty on uninterruptible power supplies has varied over the past couple of years, often depending if a machine is Single Phase or Three Phase. Few companies compete on warranty, with the focus mainly on efficiency and maintenance contracts. The standard manufacturer’s warranty is anything between 1-2 years and can even be limited to certain aspects of the machine, often excluding the more expensive items such as battery replacement. Focusing on one market, companies supplying Three Phase however now offer lengthier warranties, with the norm closer to 2 years rather than the single year.

### Difficulties faced with generator use

### Frequency variations

The voltage and frequency of the power produced by a generator depends on the engine speed. The speed is controlled by a system called a governor. Some governors are mechanical, and some are electronic. The job of the governor is to keep the voltage and frequency constant, while the load on the generator changes. This may pose a problem where, for example, the startup surge of an elevator can cause short "blips" in the frequency of the generator or the output voltage, thus affecting all other devices powered by the generator. Many radio transmission sites will have backup diesel generators – in the case of amplitude modulation(AM) radio transmitters, the load presented by the transmitters changes in line with the signal level. This leads to the scenario where the generator is constantly trying to correct the output voltage and frequency as the load changes.

It is possible for a UPS unit to be incompatible with a generator or a poor mains supply; in the event that its designers had written the microprocessor code to require exactly a 50.0 Hz (or 60.0 Hz) supply frequency in order to operate; with this condition not met the UPS could remain on battery power, being unable to reconnect the unsuitable supply voltage.

This problem of input frequency requirements should not be an issue through the use of a Double Conversion / online UPS. A UPS of this topology should be able to adapt to any input frequency, using its own internal clock source to generate the required 50 or 60 Hz supply frequency.

### Power factor

A problem in the combination of a "double conversion" UPS and a generator is the voltage distortion created by the UPS. The input of a double conversion UPS is essentially a big rectifier. The current drawn by the UPS is non-sinusoidal. This causes the voltage from the generator also to become non-sinusoidal. The voltage distortion then can cause problems in all electrical equipment connected to the generator, including the UPS itself. This level of "noise" is measured as a percentage of "Total Harmonic Distortion of the current" (THD(i)). Classic UPS rectifiers have a THD(i) level of around 25–30%. To prevent voltage distortion, this requires generators more than twice as big as the UPS.

There are several solutions to reduce the THD(i) in a double conversion UPS:

Passive power factor correction: (Passive PFC) Classic solutions such as passive filters reduce THD(i) to 5-10% at full load. They are reliable, but big and only work at full load, and present their own problems when used in tandem with generators.

Main article: Active power factor correction

An alternative solution is an active filter. Through the use of such a device, THD(i) can drop to 5% over the full power range. The newest technology in double conversion UPS units is a rectifier that doesn't use classic rectifier components (Thyristors and Diodes) but high frequency components (IGBTs). A double conversion UPS with an IGBT rectifier can have a THD(i) as small as 2%. This completely eliminates the need to oversize the generator (and transformers), without additional filters, investment cost, losses, or space.

## Communication

|  | This section requires expansion. |
| --- | --- |

Power management requires the UPS to report its status to the computer it powers, via a serial port, Ethernet or USB, and a subsystem in the OS to handle the communication and generate notifications, PM events or command an ordered shut down.[5] Manufacturers that publish their communication protocols makes integration easy. However some manufacturers like APC use proprietary protocols that make this hard.

## Calculating on-battery runtime

The energy stored in a UPS that has N rechargeable batteries can be calculated as

E = NQ1Vavg

where

Q1 is the capacity of a battery (usually measured in Ah);

Vavg is the average battery voltage during discharge.

For several reasons the effective energy that can be used from a battery UPS is lesser than the energy stored in its batteries:

Eef = ηdmaxuNQ1Vavg

where

η is the efficiency of the inverter for conversion to AC power;

dmax is max discharge percentage. Usually UPS batteries are not fully discharged as that may shorten their useful life;

u is usable capacity percentage. Lead acid batteries have a lower capacity if discharged at a high rate, which may be the case in a UPS.

The maximum on-battery runtime can now be calculated as

where

Pavg is the average power of the energy user connected to the UPS.

For example, if a UPS, which has two lead acid batteries of  and , , , , powers some electrical equipment having , we get  and .

- Notes

- ^ Modern Marvels: History Channel. "Batteries".

- ^ a b http://h20000.www2.hp.com/bc/docs/support/SupportManual/c01173322/c01173322.pdf

- ^ My Ton (Ecos Consulting), Brian Fortenbery (EPRI), William Tschudi (LNBL). DC Power for Improved Data Center Efficiency, Lawrence Berkeley National Laboratory, January 2007

- ^ PSCPower. Hybrid Rotary UPS white paper. Power Quality and Rotary Systems.

- ^ Raymond, Eric Steven. UPS HOWTO, section 3.3. The Linux Documentation Project, 2003-2007.

- ^ "How to calculate battery run-time". PowerStream Technologies. Retrieved 2010-04-26.

- References

- UPS of the front line - Plant Engineering, February 2007

- EN 62040-1-1:2006 Uninterruptible power systems (UPS) — Part 1-1: General and safety requirements for UPS used in operator access areas

- EN 62040-1-2:2003 Uninterruptible power systems (UPS) - Part 1-2: General and safety requirements for UPS used in restricted access locations

- EN 62040-2:2006 Uninterruptible power systems (UPS)- Part 2: Electromagnetic compatibility (EMC) requirements

- EN 62040-3:2001 Uninterruptible power systems (UPS) - Part 3: Method of specifying the performance and test requirements

- External links

- UPS HOWTO